Technical Information

F3X

Modbus Protocol

# VERSION HISTORY

- Version 1.0（20240109）

First Release

- Version 1.1（20240308）

Add Wi-Fi Router Name&Password

Add Wi-Fi AFCI Falut&Parameter

- Version 1.2（20240607）

Add Substate(30160)

Add Number of parallel machines(30071)

Add AFCI Firmware version(30061)

Add Start/stop heat pump(40848)

Add Emergency stop command(40849)

Add Grid Standard(40045)

Add Shadow MPPT Enable(40839)

Add Shadow MPPT Scan period(40840)

Add Remote shutdown switch Enable(40843)

Add System connection mode(40055)

Add CT Current(30183~30185)

- Version 1.3（20240629）

Add Restart command(40850)

Add First connection grid check time(40304)

Add Battery relay state(30285)

Add Battery charging available(30286)

- Version 1.4（20240717）

Add new fault(Bit27~Bit31)

- Version 1.5（20240826）

Add 30141~30147,30153,30166~30171,30197

Remove Battery relay state(30285) and Battery charging available(30286)

- Version 1.6（20241014）

Add the currently supported safety(Table 1)

Add PV input mode(40817)

- Version 1.7（20241030）

Add Max output power(40036)

Add Maxmum Apparent power(40047)

- Version 1.8（20241104）

Add Manufacturer name(40010)

Add Model name(40018)

Add Serial number(40026)

- Version 1.9（20241120）

Add Backup current R/S/T(30600~30602)

Add Wifi information(42100~42131)

Add Ciphertext(42200~42217)

- Version 1.10（20241213）

Change 40902 description

Change 40849 function(Emergency stop function enable)

Change 40903 function(EPS limt SOC on grid)

Add EPS limt SOC off grid(40905)

Add Third party meter enable(40072)

Add Third party meter active power(30110)

Add Third party meter energy(30112)

Add Backup power R/S/T(30603/30605/30607)

Add AC output power R/S/T(30609/30611/30613)

Add Backup voltage R/S/T(30615/30616/30617)

- Version 1.11（20250110）

Add Key lock enable(42201)

Add N_PE relay enable(40861)

Add Warning “First connection grid parameters error”

- Version 1.12（20250509）

Modify the grid voltage lower limit of safety

Add Fan on-off state(30625)

Add Fault_Extend(Bit)(30626)

Add Warning_Extend(Bit)(30628)

- Version 1.13（20250606）

Modify the grid voltage higher limit of safety

Add initial import/export energy from meter(40864/40866)

- Version 1.14（20250618）

Add Austrian certified related registers (40421/40443-40450)

- Version 1.15（20250704）

Add exception code registers (30872-30881)

Add exception table(three-phase and single-phase)

- Version 1.16（20250714）

Add new fault bit(bit32、bit35、bit36)

Add new warning bit(bit28)

Add new register 30630、40811(bit12)

- Version 1.17（20250715）

Modify Meter type Description(40403)

- Version 1.18（20250725）

Add new register 40552、40553

- Version 1.19（20250807）

Update register (min cos Phi enable、min cos Phi) address

Update register 40907（add new customer-mode）

Add new register 40869

- Version 1.20（20250808）

Update register 40441

- Version 1.21（20250813）

Add new safety Standard 55

- Version 1.22（20250814）

Update register 40421/40443’s unit

- Version 1.23（20250819）

Update register 40437/40438’s unit

Add Fault Code 34/36/38

Add new register 30631

Update register 40403

- Version 1.24（20250905）

Add new register 40372/40373/40451/40452/40453

Update register 30110

Update register 40403

- Version 1.25（20250908）

Add new register 40073

Update register 40403

- Version 1.26（20250919）

Add new register 30632/30634/30636/30638/30640/30642/30644/30646

Update Fault Code

- Version 1.27（20251023）

Add Exception (Single-phase) 68/69，101~113

Add new register 30075~30078, 30618~30621, 40555~40558,30117/30118

- Version 1.28（20251106）

Add new register 30036/30047/30648/30649/30650

Update register 30152

- Version 1.29（20251117）

Add new register 30652/30654/30656/30658

Update register 40403

- Version 1.30（20251125）

Add new Fault Code (Bite40)

Add new Warning Code (Bit 37/38)

- Version 1.31（20251219）

Add new Fault Code (Bit 41)

Update register 40403

- Version 1.32（20260119）

Update Fault Code (Bit 42)

Update Warning Code (Bit 11)

Add new register 40559

Update register 30063

- Version 1.33（20260206）

Add new register 40454

Update register 40410

- Version 1.34（20260327）

Add new register 40853/40854

Add new register 40973/40974/40975

Update Fault Code (Bit 43)

- Version 1.35（20260430）

# Add new register 30660～30669

# Update register 40403

- Version 1.36（20260612）

# Add new register 41000～41029

# Add new register 40074

# Update register 40403

# Table 2(Fault code) update

# TABLE OF CONTENTS

1. INFORMATION ON THIS DOCUMENT	7

2. CONNECTION PORTS	7

2.1. RS485	7

3. REGISTER ADDRESS MAP	7

3.1. Device Information(R)	7

3.2. Monitor Information & Statistics	9

3.2.1. Monitor Information(R)	9

3.2.2. Monitor Information Extend(R)	11

3.2.3. Exception Code(R)	13

3.3. Setting Parameters	13

3.3.1. Protection parameter(R/W)	13

3.3.2. Active power control(R/W)	15

3.3.3. Reactive power control(R/W)	17

3.3.4. DeviceInfo parameter(R/W)	19

3.3.5. Internal parameter(R/W)	19

3.3.6. Energy management parameter(R/W)	20

3.3.7. P1 reader parameter(R/W)	22

3.3.8. Wifi Information(R/W)	23

3.3.9. Ciphertext(R/W)	23

4. APPING EXAMPLE	29

INFORMATION ON THIS DOCUMENT

The Modbus Protocol is a communication protocol that is currently used to establish solar PV system communication, applied between HYPONTECH’s inverter and monitoring software.

The Modbus Protocol complies with RTU protocol specifications, allowing real-time status and operation statistics on monitoring interface.

CONNECTION PORTS

RS485

| RS485 Specifications |  |
| --- | --- |
| Addressing Modes | Device Register Address 1-16 |
| Baud Rate | 115200 Bit/s |
| Parity Bit | N/A |
| Data Bit | 8 |
| Stop Bit | 1 |
| Frame Format | Modbus RTU |
| Port Cabling | RS485 2W-Cabling |

REGISTER ADDRESS MAP

Device Information(R)

| Register Address | HEX | Register Name | Byte | Format | Description |
| --- | --- | --- | --- | --- | --- |
| 30010 | 753A | Manufacturer Name | 16 | ASCII*16 |  |
| 30018 | 7542 | Model Name | 16 | ASCII*16 |  |
| 30026 | 754A | Serial Number | 16 | ASCII*16 |  |
| 30036 | 7554 | Max output power | 2 | U16 |  |
| 30039 | 7557 | Software Version | 4 | U8*4 | V x.x.x.x |
| 30045 | 755D | Safety type | 2 | U16 | Table 1 |
| 30047 | 755F | Apparent power | 2 | U16 |  |
| 30055 | 7567 | Parallel Mode | 2 | U16 | 0: Independent system 1: Parallel system mode:master 2: Parallel system mode:slave |
| 30056 | 7568 | Parallel Address | 2 | U16 | Parallel mode slave address |
| 30061 | 756D | AFCI Firmware Version | 4 | U8*4 | Vx.x.x.x |
| 30063 | 756F | Serial number(E) | 16 | ASCII*16 | Serial number Expansion |
| 30071 | 7577 | Number of parallel machines | 2 | U16 |  |
| 30075 | 757B | Discharge Reted FixedQ | 2 | U16 | System Rated Reactive Power of Discharge |
| 30076 | 757C | Charge Reted FixedQ | 2 | U16 | System Rated Reactive Power of Charge |
| 30077 | 757D | Discharge Reted CosPhi | 2 | U16 | System Rated Discharge Reactive Power Factor |
| 30078 | 757E | Charge Reted CosPhi | 2 | U16 | System Rated Charge Reactive Power Factor |

Monitor Information & Statistics

Monitor Information(R)

| Register Address |  | HEX | Register Name |  | Byte |  | Unit | Format | Description |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 30100 |  | 7594 | AC Total P |  | 4 |  | W | S32 | Positive:Output Negetive :Input |  |
| 30102 |  | 7596 | AC Total S |  | 4 |  | VA | S32 | Positive:Output Negetive :Input |  |
| 30104 |  | 7598 | AC Total Q |  | 4 |  | VAR | S32 | Positive:Output Negetive :Input |  |
| 30106 |  | 759A | AC PF |  | 2 |  | 0.01 | U16 |  |  |
| 30107 |  | 759B | AC Q/PF direction |  | 2 |  |  | U16 | 1: Lag 2: Lead |  |
| 30108 |  | 759C | Grid Total Power |  | 4 |  | W | S32 | Positive value:Import from Grid Negetive value:Export to Grid |  |
| 30110 |  | 759E | Third party meter active power |  | 4 |  | W | S32 |  |  |
| 30112 |  | 75A0 | Third party meter energy |  | 4 |  | KWH | Float32 |  |  |
| 30115 |  | 75A3 | Inverter state |  | 2 |  |  | U16 | 0: Wait 1: Normal 2: Fault |  |
| 30116 |  | 75A4 | Waiting time |  | 2 |  | S | U16 |  |  |
| 30117 |  | 75A5 | Fault code |  | 2 |  |  | U16 |  |  |
| 30118 |  | 75A6 | Warning code |  | 2 |  |  | U16 |  |  |
| 30119 |  | 75A7 | PV1 voltage |  | 2 |  | 0.1V | U16 |  |  |
| 30120 |  | 75A8 | PV1 current |  | 2 |  | 0.1A | U16 |  |  |
| 30121 |  | 75A9 | PV2 voltage |  | 2 |  | 0.1V | U16 |  |  |
| 30122 |  | 75AA | PV2 current |  | 2 |  | 0.1A | U16 |  |  |
| 30123 |  | 75AB | PV3 voltage |  | 2 |  | 0.1V | U16 |  |  |
| 30124 |  | 75AC | PV3 current |  | 2 |  | 0.1A | U16 |  |  |
| 30127 |  | 75AF | PV total Power |  | 4 |  | W | S32 | W |  |
| 30129 |  | 75B1 | PV total kWH |  | 4 |  | KWH | Float32 | KWH |  |
| 30131 |  | 75B3 | AC R voltage |  | 2 |  | 0.1V | U16 |  |  |
| 30132 |  | 75B4 | AC R current |  | 2 |  | 0.1A | U16 |  |  |
| 30133 |  | 75B5 | AC S voltage |  | 2 |  | 0.1V | U16 |  |  |
| 30134 |  | 75B6 | AC S current |  | 2 |  | 0.1A | U16 |  |  |
| 30135 |  | 75B7 | AC T voltage |  | 2 |  | 0.1V | U16 |  |  |
| 30136 |  | 75B8 | AC T current |  | 2 |  | 0.1A | U16 |  |  |
| 30137 |  | 75B9 | AC Line Voltage RS |  | 2 |  | 0.1V | U16 |  |  |
| 30138 |  | 75BA | AC Line Voltage ST |  | 2 |  | 0.1V | U16 |  |  |
| 30139 |  | 75BB | AC Line Voltage TR |  | 2 |  | 0.1V | U16 |  |  |
| 30140 |  | 75BC | AC frequency |  | 2 |  | 0.01Hz | U16 |  |  |
| 30141 |  | 75BD | BUS voltage |  | 2 |  | 0.1V | U16 |  |  |
| 30142 |  | 75BE | ISO |  | 2 |  | Kohm | U16 |  |  |
| 30143 |  | 75BF | DCI |  | 2 |  | mA | S16 |  |  |
| 30144 |  | 75C0 | GFCI |  | 2 |  | mA | S16 |  |  |
| 30145 |  | 75C1 | N PE voltage |  | 2 |  | 0.1V | S16 |  |  |
| 30146 |  | 75C2 | Internal ambient temperature |  | 2 |  | 0.1℃ | S16 |  |  |
| 30147 |  | 75C3 | Internal heatsink temperature |  | 2 |  | 0.1℃ | S16 |  |  |
| 30148 |  | 75C4 | Fault(Bit) |  | 4 |  |  | U32 | Table 2 |  |
| 30150 |  | 75C6 | Warning(Bit) |  | 4 |  |  | U32 | Table 3 |  |
| 30152 |  | 75C8 | Firmware Update Sate |  | 2 |  |  | U16 | 0: Idle 1: Download finished 2: Update finished 3: Download fail |  |
| 30153 |  | 75C9 | Internal boost-module temperature |  | 2 |  | 0.1℃ | S16 |  |  |
| 30154 |  | 75CA | E-total of AC Output |  | 4 |  | kWh | Float32 |  |  |
| 30156 |  | 75CC | Import Energy from Grid (meter) |  | 4 |  | kWh | Float32 |  |  |
| 30158 |  | 75CE | Export Energy to Grid (meter) |  | 4 |  | kWh | Float32 |  |  |
| 30160 | 75D0 |  |  | AC Output Substate |  | 2 |  | Enum16 | 0: Null 1: Normal at Grid tied mode 2: Normal at Back up mode |
| 30161 | 75D1 |  |  | Battery State |  | 2 |  | Enum16 | Battery status 0:Sleep 1: Charging 2: Discharging 3: Idle 4: Standby 5: Run 6: Fault 7: Offline |
| 30162 | 75D2 |  |  | Battery charge/discharge power |  | 4 | W | S32 | Positive value: Discharge Negetive value: Charge |
| 30164 | 75D4 |  |  | Battery Voltage |  | 2 | 0.1V | U16 |  |
| 30165 | 75D5 |  |  | Battery charge/discharge current |  | 2 | 0.1A | S16 | Positive value: Discharge Negetive value: Charge |
| 30166 | 75D6 |  |  | Charge forbidden mask |  | 2 |  | U16 |  |
| 30167 | 75D7 |  |  | Discharge forbidden mask |  | 2 |  | U16 |  |
| 30168 | 75D8 |  |  | Forced charge request |  | 2 |  | U16 |  |
| 30170 | 75DA |  |  | EPS Volt |  | 2 | 0.1V | U16 |  |
| 30171 | 75DB |  |  | EPS Freq |  | 2 | 0.01Hz | U16 |  |
| 30172 |  | 75DC |  | EPS Total Power |  | 4 | W | S32 | Positive value: Output Negetive value: Input |
| 30174 |  | 75DE |  | Battery Charge Energy |  | 4 | KWH | Float32 | Battery Charge |
| 30176 |  | 75E0 |  | Battery Discharge Energy |  | 4 | KWH | Float32 | Battery Discharge |
| 30178 |  | 75E2 |  | Battery Charge Energy From AC |  | 4 | KWH | Float32 |  |
| 30180 |  | 75E4 |  | EPS Output Energy |  | 4 | KWH | Float32 |  |
| 30182 |  | 75E6 |  | SOC |  | 2 | % | U16 | Battery SOC |
| 30183 |  | 75E7 |  | CT Current R |  | 2 | 0.1A | S16 |  |
| 30184 |  | 75E8 |  | CT Current S |  | 2 | 0.1A | S16 |  |
| 30185 |  | 75E9 |  | CT Current T |  | 2 | 0.1A | S16 |  |
| 30186 |  | 75EA |  | Grid Power R |  | 4 | W | S32 | Positive value: Import from Grid Negetive value: Export to Grid |
| 30188 |  | 75EC |  | Grid Power S |  | 4 | W | S32 | Positive value: Import from Grid Negetive value: Export to Grid |
| 30190 |  | 75EE |  | Grid Power T |  | 4 | W | S32 | Positive value: Import from Grid Negetive value: Export to Grid |
| 30197 |  | 75F5 |  | Bus P_to_M voltage |  | 2 | 0.1V | U16 |  |

Monitor Information Extend(R)

| Register Address | HEX | Register Name | Byte | Unit | Format | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 30600 | 7788 | Backup current R | 2 | 0.1A | U16 | Backup load current |
| 30601 | 7789 | Backup current S | 2 | 0.1A | U16 | Backup load current |
| 30602 | 778A | Backup current T | 2 | 0.1A | U16 | Backup load current |
| 30603 | 778B | Backup power R | 4 | W | S32 | Backup load power |
| 30605 | 778D | Backup power S | 4 | W | S32 | Backup load power |
| 30607 | 778F | Backup power T | 4 | W | S32 | Backup load power |
| 30609 | 7791 | AC output power R | 4 | W | S32 | output active power |
| 30611 | 7793 | AC output power S | 4 | W | S32 | output active power |
| 30613 | 7795 | AC output power T | 4 | W | S32 | output active power |
| 30615 | 7797 | Backup voltage R | 2 | 0.1V | U16 | Backup load voltage |
| 30616 | 7798 | Backup voltage S | 2 | 0.1V | U16 | Backup load voltage |
| 30617 | 7799 | Backup voltage T | 2 | 0.1V | U16 | Backup load voltage |
| 30618 | 779A | Meter R voltage | 2 | 0.1V | U16 | Phase R Voltage_meter |
| 30619 | 779B | Meter S voltage | 2 | 0.1V | U16 | Phase S Voltage_meter |
| 30620 | 779C | Meter T voltage | 2 | 0.1V | U16 | Phase T Voltage_meter |
| 30621 | 779D | Meter Reactive Power | 4 | Var | S32 | Total Reactive Power_meter |
| 30625 | 77A1 | Fan on-off state | 2 |  | U16 | 0: Turn off 1: Turn on |
| 30626 | 77A2 | Fault_Extend(Bit) | 4 |  | U32 | Table 2 |
| 30628 | 77A4 | Warning_Extend(Bit) | 4 |  | U32 | Table 3 |
| 30630 | 77A6 | Min CosPhi(P) cosPhi | 2 | 0.01 | U16 |  |
| 30631 | 77A7 | Parallel_Salve State | 2 |  | U16 | 从机告警码，bit位标志从机非Normal状态 |
| 30632 | 77A8 | Parallel_System PV Total Power | 4 | W | S32 | 并机系统PV侧直流总功率 |
| 30634 | 77AA | Parallel_System Battery charge/discharge Total Power | 4 | W | S32 | 并机系统电池充放电总功率 Positive value:Discharge Negetive value:Charge |
| 30636 | 77AC | Parallel_System Backup R Total power/Single-phase Total power | 4 | W | S32 | 并机系统Backup R相总功率/单相总功率 |
| 30638 | 77AE | Parallel_System Backup S Total power | 4 | W | S32 | 并机系统Backup S相总功率 |
| 30640 | 77B0 | Parallel_System Backup T Total power | 4 | W | S32 | 并机系统Backup T相总功率 |
| 30642 | 77B2 | Parallel_System R Output P Total power/Single-phase Output P Total power | 4 | W | S32 | 并机系统 R相逆变总功率/单相逆变总功率 |
| 30644 | 77B4 | Parallel_System S Output P Total power | 4 | W | S32 | 并机系统 S相逆变总功率 |
| 30646 | 77B6 | Parallel_System T Output P Total power | 4 | W | S32 | 并机系统 T相逆变总功率 |
| 30648 | 77B8 | Parallel_System Batt Total AH | 2 | AH | U16 | 并机系统 电池容量总AH |
| 30649 | 77B9 | Parallel_System Batt Total KWH | 2 | 0.01KWH | U16 | 并机系统 电池容量总KWH |
| 30650 | 77BA | Parallel_System PCS rate power Total | 4 | W | U32 | 并机系统 PCS额定功率总容量 |
| 30652 | 77BC | Parallel_System Output Q Total power | 4 |  | S32 | 并机系统 逆变总无功功率 |
| 30654 | 77BE | ACC_R_Power | 4 | W | S32 | ACC_第三方电表 R相功率 |
| 30656 | 77C0 | ACC_S_Power | 4 | W | S32 | ACC_第三方电表 S相功率 |
| 30658 | 77C2 | ACC_T_Power | 4 | W | S32 | ACC_第三方电表 T相功率 |
| 30660 | 77C4 | Meter PF | 2 | 0.001 | S16 | 电表测量PF值（EM530/EM540） |
| 30661 | 77C5 | Meter GridFrequency | 2 | 0.1Hz | U16 | 电表测量电网频率值（EM530/EM540） |
| 30662 | 77C6 | Grid to Battery Energy | 4 | KWH | Float32 | 电网流向电池的电量 |
| 30664 | 77C8 | Battery to Grid Energy | 4 | KWH | Float32 | 电池流向电网的电量 |
| 30666 | 77CA | Grid to EPS Energy | 4 | KWH | Float32 | 电网流向EPS负载的电量 |
| 30668 | 77CC | Battery to EPS Energy | 4 | KWH | Float32 | 电池流向EPS负载的电量 |

Exception Code(R)

| Register Address | HEX | Register Name | Byte | Unit | Format | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 30872 | 7898 | Exception Code[0] | 2 |  | U16 | The previous exception |
| 30873 | 7899 | Exception Code[1] | 2 |  | U16 | The first two exception |
| 30874 | 789A | Exception Code[2] | 2 |  | U16 | The first three exception |
| 30875 | 789B | Exception Code[3] | 2 |  | U16 | The first four exception |
| 30876 | 789C | Exception Code[4] | 2 |  | U16 | The first five exception |
| 30877 | 789D | Exception Code[5] | 2 |  | U16 | The first six exception |
| 30878 | 789E | Exception Code[6] | 2 |  | U16 | The first seven exception |
| 30879 | 789F | Exception Code[7] | 2 |  | U16 | The first eight exception |
| 30880 | 78A0 | Exception Code[8] | 2 |  | U16 | The first nine exception |
| 30881 | 78A1 | Exception Code[9] | 2 |  | U16 | The first ten exception |

Setting Parameters

Protection parameter(R/W)

| Register Address | HEX | Register Name | Byte | Unit | Format | Description |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 40300 | 9D6C | First connection voltage upper value | 2 | 0.1V | U16 | 50-350V |  |
| 40301 | 9D6D | First connection voltage lower value | 2 | 0.1V | U16 | 50-350V |  |
| 40302 | 9D6E | First connection frequency upper value | 2 | 0.01Hz | U16 | 45-65Hz |  |
| 40303 | 9D6F | First connection frequency lower value | 2 | 0.01hz | U16 | 45-65Hz |  |
| 40304 | 9D70 | First connection grid check time | 4 | mS | U32 | - |  |
| 40306 | 9D72 | First connection time | 2 | S | U16 | - |  |
| 40307 | 9D73 | First connection power increase rate | 2 | 0.1%Pn/min | U16 | - |  |
| 40310 | 9D76 | Over voltage protection value 1 | 2 | 0.1V | U16 | 50-350V |  |
| 40311 | 9D77 | Over voltage trigger time 1 | 4 | mS | U32 | - |  |
| 40313 | 9D79 | Over voltage protection value 2 | 2 | 0.1V | U16 | 50-350V |  |
| 40314 | 9D7A | Over voltage trigger time 2 | 4 | mS | U32 | - |  |
| 40316 | 9D7C | Over voltage protection value 3 | 2 | 0.1V | U16 | 50-300V |  |
| 40317 | 9D7D | Over voltage trigger time 3 | 4 | mS | U32 | - |  |
| 40319 | 9D7F | Under voltage protection value 1 | 2 | 0.1V | U16 | 50-350V |  |
| 40320 | 9D80 | Under voltage trigger time 1 | 4 | mS | U32 | - |  |
| 40322 | 9D82 | Under voltage protection value | 2 | 0.1V | U16 | 50-350V |  |
| 40323 | 9D83 | Under voltage trigger time 2 | 4 | mS | U32 | - |
| 40325 | 9D85 | Under voltage protection value 3 | 2 | 0.1V | U16 | 50-350V |
| 40326 | 9D86 | Under voltage trigger time 3 | 4 | mS | U32 | - |
| 40328 | 9D88 | Over frequency protection value 1 | 2 | 0.01Hz | U16 | 45-65Hz |
| 40329 | 9D89 | Over frequency trigger time 1 | 4 | mS | U32 | - |
| 40331 | 9D8B | Over frequency protection value 2 | 2 | 0.01Hz | U16 | 45-65Hz |
| 40332 | 9D8C | Over frequency trigger time 2 | 4 | mS | U32 | - |
| 40334 | 9D8E | Over frequency protection value 3 | 2 | 0.01Hz | U16 | 45-65Hz |
| 40335 | 9D8F | Over frequency trigger time 3 | 4 | mS | U32 | - |
| 40337 | 9D91 | Under frequency protection value 1 | 2 | 0.01Hz | U16 | 45-65Hz |
| 40338 | 9D92 | Under fequency trigger time 1 | 4 | mS | U32 | - |
| 40340 | 9D94 | Under frequency protection value 2 | 2 | 0.01Hz | U16 | 45-65Hz |
| 40341 | 9D95 | Under frequency trigger time 2 | 4 | mS | U32 | - |
| 40343 | 9D97 | Under frequency protection value 3 | 2 | 0.01Hz | U16 | 45-65Hz |
| 40344 | 9D98 | Under frequency trigger time 3 | 4 | mS | U32 | - |
| 40346 | 9D9A | 10min average voltage protection value | 2 | 0.1V | U16 | 50-350V |
| 40347 | 9D9B | 10min average voltage trigger time | 4 | mS | U32 | - |
| 40349 | 9D9D | Over voltage recovery value | 2 | 0.1V | U16 | 50-350V |
| 40350 | 9D9E | Under voltage recovery value | 2 | 0.1V | U16 | 50-350V |
| 40351 | 9D9F | Over frequency recovery value | 2 | 0.01Hz | U16 | 45-65Hz |
| 40352 | 9DA0 | Under frequency recovery value | 2 | 0.01Hz | U16 | 45-65Hz |
| 40353 | 9DA1 | Grid faut recovery time | 4 | mS | U32 | - |
| 40356 | 9DA4 | Grid fault reconnection time | 2 | S | U16 | - |
| 40357 | 9DA5 | Power recovery rate after reconnect | 2 | 0.1%Pn/min | U16 | - |
| 40370 | 9DB2 | ExternalSignal of CEI | 2 | - | U16 | 0-1(1 as default) |
| 40371 | 9DB3 | LocalControl of CEI | 2 | - | U16 | 0-1(0 as default) |
| 40372 | 9DB4 | FreGVREN | 2 | - | U16 | 0: Disable 1: Enable Grid Frequency Protection模块内设置 |
| 40373 | 9DB5 | FreqMaxVR | 2 | 0.1Hz/s | U16 | Threshold of frequency change rate of grid voltage 5-50 Grid Frequency Protection 模块内设置 |

Active power control(R/W)

| Register Address | HEX | Register Name | Byte | Unit | Format | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 40400 | 9DD0 | Active power control mode | 2 | - | U16 | 0: No used 1: Fixed active Power 2: DRED 3: Meter/CT 4: Plant control |
| 40401 | 9DD1 | Meter limit power | 4 | W | S32 |  |
| 40403 | 9DD3 | Meter type | 2 | - | - | 0: SDM120 1: SDM630 2: Internal CT 5: ACC(Three Phase Only) 6: DTSU-666 7：CT-ACC(single phase ) 8：EM530(EM540) 9：SDM01 10：SEM3-2L 11：SDM120CT 12: SDM120CT-LoRa 13: P1 Meter |
| 40404 | 9DD4 | Plant limit power | 2 |  |  |  |
| 40405 | 9DD5 | Meter limit mode | 2 |  | U16 | 0: Total three phases active power control 1: Minimum phase active power control 2: No feeder control |
| 40406 | 9DD6 | Startup loading slope | 2 | 0.1%Pn/min | U16 |  |
| 40408 | 9DD8 | Active power Increase Rate | 2 | 0.1%Pn/min | U16 |  |
| 40409 | 9DD9 | Active power Decrease Rate | 2 | 0.1%Pn/min | U16 |  |
| 40410 | 9DDA | Fixed active power | 2 | %Pn | U16 | 0-100; AC侧放电功率限制 |
| 40411 | 9DDB | Over frequency response enable | 2 | - | U16 | 0: Disable 1: Enable |
| 40412 | 9DDC | Fixed active power response time | 2 | S | U16 | - |
| 40413 | 9DDD | Over frequency response mode | 2 |  | U16 | 1: Hysteresis mode 2: No hysteresis mode |
| 40414 | 9DDE | Over frequency response Fstart | 2 | 0.01Hz | U16 | 45-65Hz |
| 40415 | 9DDF | Over frequency response Fstop | 2 | 0.01Hz | U16 | 45-65Hz |
| 40416 | 9DE0 | Over frequency response P drop rate | 2 | 0.1%Pn/min | U16 | - |
| 40417 | 9DE1 | Over frequency response Fback | 2 | 0.01Hz | U16 | 45-65Hz |
| 40418 | 9DE2 | Over frequency response P recovery rate | 2 | 0.1%Pn/min | U16 | - |
| 40419 | 9DE3 | Over frequency response delay time | 2 | S | U16 |  |
| 40420 | 9DE4 | Over frequency recovery delay time | 2 | S | U16 |  |
| 40421 | 9DE5 | Over frequency s | 2 | % | U16 | 0-100 |
| 40422 | 9DE6 | P(U) curve enable | 2 | - | U16 | 0: Disable 1: Enable |
| 40423 | 9DE7 | P(U) curve P 1 | 2 | %Pn | U16 | 0-100 |
| 40424 | 9DE8 | P(U) curve U 1 | 2 | 0.1V | U16 | 50-350V |
| 40425 | 9DE9 | P(U) curve P 2 | 2 | %Pn | U16 | 0-100 |
| 40426 | 9DEA | P(U) curve U 2 | 2 | 0.1V | U16 | 50-350V |
| 40427 | 9DEB | P(U) curve P 3 | 2 | %Pn | U16 | 0-100 |
| 40428 | 9DEC | P(U) curve U 3 | 2 | 0.1V | U16 | 50-350V |
| 40429 | 9DED | P(U) curve P 4 | 2 | %Pn | U16 | 0-100 |
| 40430 | 9DEE | P(U) curve U 4 | 2 | 0.1V | U16 | 50-350V |
| 40431 | 9DEF | P(U) P response time | 2 | S | U16 | 0-60S |
| 40432 | 9DF0 | Under Frequency Enable | 2 |  | U16 | 0: Disable 1: Enable |
| 40433 | 9DF1 | Under Frequency Mode | 2 |  | U16 | 1: Hysteresis mode 2: No hysteresis mode |
| 40434 | 9DF2 | Under Frequency Fstart | 2 | 0.01Hz | U16 | 45-65Hz |
| 40435 | 9DF3 | Under Frequency Fstop | 2 | 0.01Hz | U16 | 45-65Hz |
| 40436 | 9DF4 | Under Frequency Fback | 2 | 0.01Hz | U16 | 45-65Hz |
| 40437 | 9DF5 | Under Frequency response delay time | 2 | S | U16 |  |
| 40438 | 9DF6 | Under Frequency recovery delay time | 2 | S | U16 |  |
| 40439 | 9DF7 | Under Frequency increase rate | 2 | 0.1%Pn/min | U16 |  |
| 40440 | 9DF8 | Under Frequency decrease rate | 2 | 0.1%Pn/min | U16 |  |
| 40441 | 9DF9 | Fixed_Active_power_value | 4 | S | S32 |  |
| 40443 | 9DFB | Under Frequency s | 2 | % | U16 | 0-100 |
| 40444 | 9DFC | HVRT Volt Upper Percent | 2 | %Un | U16 | 100%~200% |
| 40445 | 9DFD | LVRT Volt Lower Percent | 2 | %Un | U16 | 1%~100% |
| 40446 | 9DFE | HVRT Volt recovery Upper Percent | 2 | %Un | U16 | 100%~200% |
| 40447 | 9DFF | LVRT Volt recovery Lower Percent | 2 | %Un | U16 | 1%~100% |
| 40448 | 9E00 | LVRT Q Response time Cnt | 2 |  | U16 | 0~65535 |
| 40449 | 9E01 | Over frequency P referance | 2 |  | U16 | 0: current power；1：maximum power；2：ON_PM_PLUS_PCMA |
| 40450 | 9E02 | Under Frequency P referance | 2 |  | U16 | 0: current power；1：maximum power；2：ON_PM_PLUS_PCMA |
| 40451 | 9E03 | Zero current mode enable | 2 |  | U16 | 零电流模式使能； |
| 40452 | 9E04 | Static voltage range over-voltage | 2 |  | U16 | 过压静态电压范围； |
| 40453 | 9E05 | Static voltage range under-voltage | 2 |  | U16 | 欠压静态电压范围； |
| 40454 | 9E06 | ImpACLimit | 2 | %Pn | U16 | 0-100; AC侧取电功率限制 |

Reactive power control(R/W)

| Register Address | HEX | Register Name | Byte | Unit | Format |  | Description |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 40510 | 9E3E | Reactive power control mode | 2 |  | U16 |  | 0: No used 1: Fixed cosPhi 2: Fixed Q 3: Cosphi(P) 4: Q(U) 5: DRED |
| 40511 | 9E3F | DRM7 Q | 2 | %Pn | U16 |  | 0-60 |
| 40512 | 9E40 | Fixed cosPhi | 2 | 0.01 | U16 |  | 80-100 |
| 40513 | 9E41 | Fixed cosPhi phase | 2 |  | U16 |  | 1: Lag 2: Lead |
| 40514 | 9E42 | CosPhi response time | 2 | S | U16 |  | 0-100S |
| 40515 | 9E43 | Fixed Q | 2 | %Pn | U16 |  | 0-60 |
| 40516 | 9E44 | Fixed Q phase | 2 |  | U16 |  | 1: Lag 2: Lead |
| 40517 | 9E45 | Q response time | 2 | S | U16 |  | 0-60S |
| 40518 | 9E46 | CosPhi(P) cosPhi 1 | 2 | 0.01 | U16 |  | 80-100 |
| 40519 | 9E47 | CosPhi(P) cosPhi 1 phase | 2 |  | U16 |  | 1: Lag 2: Lead |
| 40520 | 9E48 | CosPhi(P) P 1 | 2 | %Pn | U16 |  | 0-100 |
| 40521 | 9E49 | CosPhi(P) cosPhi 2 | 2 | 0.01 | U16 |  | 80-100 |
| 40522 | 9E4A | CosPhi(P) cosPhi 2 phase | 2 |  | U16 |  | 1: Lag 2: Lead |
| 40523 | 9E4B | CosPhi(P) P 2 | 2 | %Pn | U16 |  | 0-100 |
| 40524 | 9E4C | CosPhi(P) cosPhi 3 | 2 | 0.01 | U16 | 80-100 |  |
| 40525 | 9E4D | CosPhi(P) cosPhi 3 phase | 2 |  | U16 | 1: Lag 2: Lead |  |
| 40526 | 9E4E | CosPhi(P) P 3 | 2 | %Pn | U16 | 0-100 |  |
| 40527 | 9E4F | CosPhi(P) cosPhi 4 | 2 | 0.01 | U16 | 80-100 |  |
| 40528 | 9E50 | CosPhi(P) cosPhi 4 phase | 2 |  | U16 | 1: Lag 2: Lead |  |
| 40529 | 9E51 | CosPhi(P) P 4 | 2 | %Pn | U16 | 0-100 |  |
| 40530 | 9E52 | CosPhi(P) cosPhi response time | 2 | S | U16 | 0-60S |  |
| 40531 | 9E53 | CosPhi Mode | 2 | S | U16 | 1: Cosphi-P Hypst 0: Cosphi-P NoHypst |  |
| 40532 | 9E54 | Q(U) Q response time 2 | 2 | S | U16 |  |  |
| 40533 | 9E55 | Q(U) mode | 2 | - | U16 | 0: P lock-in lock-out Disable 1: P lock-in lock-out Enable |  |
| 40534 | 9E56 | Q(U) Q 1 | 2 | %Pn | U16 | 0-60 |  |
| 40535 | 9E57 | Q(U) Q 1 phase | 2 |  | U16 | 1: Lag 2: Lead |  |
| 40536 | 9E58 | Q(U) U 1 | 2 | 0.1V | U16 | 100-300V |  |
| 40537 | 9E59 | Q(U) Q 2 | 2 | %Pn | U16 | 0-60 |  |
| 40538 | 9E5A | Q(U) Q 2 phase | 2 |  | U16 | 1: Lag 2: Lead |  |
| 40539 | 9E5B | Q(U) U 2 | 2 | 0.1V | U16 | 100-300V |  |
| 40540 | 9E5C | Q(U) Q 3 | 2 | %Pn | U16 | 0-60 |  |
| 40541 | 9E5D | Q(U) Q 3 phase | 2 |  | U16 | 1: Lag 2: Lead |  |
| 40542 | 9E5E | Q(U) U 3 | 2 | 0.1V | U16 | 100-300V |  |
| 40543 | 9E5F | Q(U) Q 4 | 2 | %Pn | U16 | 0-60 |  |
| 40544 | 9E60 | Q(U) Q 4 phase | 2 |  | U16 | 1: Lag 2: Lead |  |
| 40545 | 9E61 | Q(U) U 4 | 2 | 0.1V | U16 | 100-300V |  |
| 40546 | 9E62 | Q(U) Q response time | 2 | S | U16 | 0~60S |  |
| 40547 | 9E63 | Lock In Pn | 2 | %Pn | U16 |  |  |
| 40548 | 9E64 | Lock Out Pn | 2 | %Pn | U16 |  |  |
| 40549 | 9E65 | CosPhi Lock In Un | 2 | 0.1V | U16 | 0-300V and greater than CosPhi Lock Out Un |  |
| 40550 | 9E66 | CosPhi Lock Out Un | 2 | 0.1V | U16 | 0-300V |  |
| 40553 | 9E69 | min cos Phi Enable | 2 |  | U16 | 0: Disable 1: Enable |  |
| 40554 | 9E6A | min cos Phi value | 2 | 0.01 | S16 | 0~100 |  |
| 40555 | 9E6B | Discharge Max FixedQ | 2 |  | U16 | 0~15000 |  |
| 40556 | 9E6C | Charge Max FixedQ | 2 |  | U16 | 0~15000 |  |
| 40557 | 9E6D | Discharge Max CosPhi | 2 | 0.01 | U16 | 0~100 |  |
| 40558 | 9E6E | Charge Max CosPhi | 2 | 0.01 | U16 | 0~100 |  |
| 40559 | 9E6F | enwg 14a Enable | 2 |  | U16 | 0：Disable 1：Enable |  |

DeviceInfo parameter(R/W)

| Register Address | HEX | Register Name | Byte | Unit | Format | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 40010 | 9C4A | Manufacturer name | 16 |  | ASCII |  |
| 40018 | 9C52 | Model name | 16 |  | ASCII |  |
| 40026 | 9C5A | Serial number | 16 |  | ASCII |  |
| 40036 | 9C64 | Max output power | 2 | W | U16 |  |
| 40045 | 9C6D | Grid Standard | 2 |  | U16 | Table 1 |
| 40047 | 9C6F | Maxmum Apparent power | 2 | VA | U16 |  |
| 40055 | 9C77 | System connection mode | 2 |  | U16 | 0: Independent system 1: Parallel system mode:master 2: Parallel system mode:slave |
| 40072 | 9C88 | Third party meter enable | 2 |  | U16 | 0: Disable 1: Enable |
| 40073 | 9C89 | Import max current from grid | 2 | 0.1A | U16 | Range：160~240 Resolution：0.1A Default：200 |
| 40074 | 9C8A | Grid phase order enable | 2 |  | U16 | 0:Disable 1:Enable |

Internal parameter(R/W)

| Register Address | HEX | Register Name | Byte | Unit | Format | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 40811 | 9F6B | Voltage Ride-Through Enable | 2 |  | U16 | Bit12: LVRT Enable |
| 40817 | 9F71 | PV input mode | 2 |  | U16 | 0: Independent mode 1: Parallel mode |
| 40819 | 9F73 | Start/stop command | 2 |  | U16 | 0: Start 1: Stop |
| 40839 | 9F87 | Shadow MPPT Enable | 2 |  | U16 | 0: Disable 1: Enable |
| 40840 | 9F88 | Shadow MPPT Scan period | 2 | s | U16 | Range:60s~65535s |
| 40843 | 9F8B | Remote shutdown switch Enable | 2 |  | U16 | 0: Disable 1: Enable |
| 40844 | 9F8C | AutoTest Enable of CEI | 2 |  | U16 | Set 1 then auto changed to 0 |
| 40845 | 9F8D | AFCI Function Enable | 2 |  | U16 | 0: Disable 1: Enable |
| 40846 | 9F8E | AFCI Fault Clear | 2 |  | U16 | 0: Disable 1: Enable |
| 40848 | 9F90 | Start/stop heat pump | 2 |  | U16 | 0: Stop 1: Start |
| 40849 | 9F91 | Emergency stop function enable | 2 |  | U16 | 0: Disable 1: Enable |
| 40850 | 9F92 | Restart command | 2 |  | U16 | 0: Disable 1: Enable |
| 40853 | 9F95 | GLS Limitation Schemes Enable | 2 |  | U16 | 0: Disable 1: Enable |
| 40854 | 9F96 | GLS System State Reset | 2 |  | U16 | 0: Reserve 1: Reset |
| 40861 | 9F9D | N_PE relay enable | 2 |  | U16 | 0: Disable 1: Enable |
| 40864 | 9FA0 | Initial import energy from meter | 4 | kWh | Float32 |  |
| 40866 | 9FA2 | Initial export energy from meter | 4 | kWh | Float32 |  |
| 40869 | 9FA5 | Meter_CT_Direction——Enable | 2 |  | U16 | 0: Disable(Default) 1: Enable |

Energy management parameter(R/W)

| Register Address |  | HEX | Register Name |  | Byte |  | Unit | Format |  |  |  | Description |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 40900 |  | 9FC4 | BatteryModel |  | 2 |  |  | U16 |  |  |  | 0: No battery 1: Battery simulator 3: Pylon |
| 40901 |  | 9FC5 | Charge/Dischage Power Reference |  | 2 |  | 0.1Pn% | S16 |  |  |  | When EMS mode set to 4 , must set this register |
| 40902 |  | 9FC6 | Charge limit SOC |  | 2 |  | % | U16 |  |  |  | Default value: 100 |
| 40903 |  | 9FC7 | EPS limit SOC on grid |  | 2 |  | % | U16 |  |  |  | Default vaule:10 |
| 40904 |  | 9FC8 | EPS enable |  | 2 |  |  | U16 |  |  |  | Set available not Normal Mode 0: Disable EPS output 1: Enable EPS output |
| 40905 |  | 9FC9 | EPS limit SOC off grid |  | 2 |  | % | U16 |  |  |  | Default vaule:10 |
| 40907 | 9FCB |  |  | EMS mode |  | 2 |  |  | U16 |  | 0: Self-Consumption 1: Back up mode 2: Off-Grid mode 3: Feed in priority mode 4: User mode 5: PN-Customer mode |  |
| 40908 | 9FCC |  |  | Time 1 enable |  | 2 |  |  | U16 |  |  |  |
| 40909 | 9FCD |  |  | Time 1 start time |  | 2 |  |  | U16 |  | High byte: Hour Low byte: Minute For example 14:30 Register value should be 0xE1E |  |
| 40910 | 9FCE |  |  | Time 1 end time |  | 2 |  |  | U16 |  | High byte: Hour ow byte: Minute For example 15:30 Register value should be 0xF1E |  |
| 40911 | 9FCF |  |  | Time 1 mode |  | 2 |  |  | U16 |  | Charge or Discharge 0: Charge 1: Discharge |  |
| 40912 | 9FD0 |  |  | Time 1 power |  | 2 | 0.1%Pn |  | U16 |  |  |  |
| 40913 | 9FD1 |  |  | Time 1 weekday |  | 2 |  |  | U16 |  | Bit 0:Sunday Bit 1:Monday … Bit 7:Saturday |  |
| 40914 | 9FD2 |  |  | Time 2 enable |  | 2 |  |  | U16 |  |  |  |
| 40915 | 9FD3 |  |  | Time 2 start time |  | 2 |  |  | U16 |  |  |  |
| 40916 | 9FD4 |  |  | Time 2 end time |  | 2 |  |  | U16 |  |  |  |
| 40917 | 9FD5 |  |  | Time 2 mode |  | 2 |  |  | U16 |  |  |  |
| 40918 | 9FD6 |  |  | Time 2 power |  | 2 | 0.1%Pn |  | U16 |  |  |  |
| 40919 | 9FD7 |  |  | Time 2 weekday |  | 2 |  |  | U16 |  |  |  |
| 40920 | 9FD8 |  |  | Time 3 enable |  | 2 |  |  | U16 |  |  |  |
| 40921 | 9FD9 |  |  | Time 3 start time |  | 2 |  |  | U16 |  |  |  |
| 40922 | 9FDA |  |  | Time 3 end time |  | 2 |  |  | U16 |  |  |  |
| 40923 | 9FDB |  |  | Time 3 mode |  | 2 |  |  | U16 |  |  |  |
| 40924 | 9FDC |  |  | Time 3 power |  | 2 | 0.1%Pn |  | U16 |  |  |  |
| 40925 | 9FDD |  |  | Time 3 weekday |  | 2 |  |  | U16 |  |  |  |
| 40926 | 9FDE |  |  | Time 4 enable |  | 2 |  |  | U16 |  |  |  |
| 40927 | 9FDF |  |  | Time 4 start time |  | 2 |  |  | U16 |  |  |  |
| 40928 | 9FE0 |  |  | Time 4 end time |  | 2 |  |  | U16 |  |  |  |
| 40929 | 9FE1 |  |  | Time 4 mode |  | 2 |  |  | U16 |  |  |  |
| 40930 | 9FE2 |  |  | Time 4 power |  | 2 | 0.1%Pn |  | U16 |  |  |  |
| 40931 | 9FE3 |  |  | Time 4 weekday |  | 2 |  |  | U16 |  |  |  |
| 40932 | 9FE4 |  |  | RealTime Year |  | 2 |  |  | U16 |  | For example 2021 Register value should be 2021 |  |
| 40933 | 9FE5 |  |  | RealTime Date |  | 2 |  |  |  | U16 | High byte: Month Low byte: Day For example 4-28 Register value should be 0x41C |  |
| 40934 | 9FE6 |  |  | RealTime Hour_Minute |  | 2 |  |  |  | U16 | High byte: Hour Low byte: Minute For example 14:30 Register value should be 0xE1E |  |
| 40935 | 9FE7 |  |  | RealTime Secon_Weekday |  | 2 |  |  |  | U16 | High byte: Second Low byte: Weekday For example 59s Wednesday Register value should be 0x3803 Note:Sunday is the first day of one week |  |
| 40936 | 9FE8 |  |  | Reset reconnect time after back-up overload |  | 2 |  |  |  | U16 | 0: Null 1: Reset reconnect time after back-up overload |  |
| 40937 | 9FE9 |  |  | ImpWMeterLim |  | 4 |  |  |  | U32 | Limit the power get from the grid |  |
| 40973 | A00D |  |  | Peak-Shaving Enable |  | 2 |  |  |  | U16 | 0: Disable 1: Enable |  |
| 40974 | A00E |  |  | Safety SOC Limit |  | 2 | % |  |  | U16 | 10-100 |  |
| 40975 | A00F |  |  | Safety Meter Power Limit |  | 2 | W |  |  | U16 | 0~60000 |  |

P1 reader parameter(R/W)

| Register Address | HEX | Register Name | Byte | Unit | Format | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 41000 | A028 | 正向低费率累积电能kWh | 4 | 0.01kWh | U32 |  |
| 41002 | A02A | 正向正常费率累积电能kWh | 4 | 0.01kWh | U32 |  |
| 41004 | A02C | 反向低费率累积电能kWh | 4 | 0.01kWh | U32 |  |
| 41006 | A02E | 反向正常费率累积电能kWh | 4 | 0.01kWh | U32 |  |
| 41008 | A030 | 电网L1电流A | 2 | 0.01A | U16 |  |
| 41009 | A031 | 电网L2电流A | 2 | 0.01A | U16 |  |
| 41010 | A032 | 电网L3电流A | 2 | 0.01A | U16 |  |
| 41011 | A033 | 电网L1电压V | 2 | 0.01V | U16 |  |
| 41012 | A034 | 电网L2电压V | 2 | 0.01V | U16 |  |
| 41013 | A035 | 电网L3电压V | 2 | 0.01V | U16 |  |
| 41014 | A036 | 正向总有功功率kW | 4 | 0.01kW | U32 |  |
| 41016 | A038 | 反向总有功功率kW | 4 | 0.01kW | U32 |  |
| 41018 | A03A | 电网L1正向有功功率W | 4 | 0.01W | U32 |  |
| 41020 | A03C | 电网L2正向有功功率W | 4 | 0.01W | U32 |  |
| 41022 | A03E | 电网L3正向有功功率W | 4 | 0.01W | U32 |  |
| 41024 | A040 | 电网L1反向有功功率W | 4 | 0.01W | U32 |  |
| 41026 | A042 | 电网L2反向有功功率W | 4 | 0.01W | U32 |  |
| 41028 | A044 | 电网L3反向有功功率W | 4 | 0.01W | U32 |  |

Wifi Information(R/W)

| Register Address | HEX | Register Name | Byte | Unit | Format | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 42100 | A474 | Wifi ssid | 32 |  | ASCII |  |
| 42116 | 9C52 | Wifi key | 32 |  | ASCII |  |

Ciphertext(R/W)

| Register Address | HEX | Register Name | Byte | Unit | Format | Description |
| --- | --- | --- | --- | --- | --- | --- |
| 42200 | A4D8 | Ciphertext type | 2 |  | U16 | 1: SN 2: Power |
| 42201 | A4D9 | Key lock enable | 2 |  | U16 | 0: Disable 1: Enable |
| 42202 | A4DA | Ciphertext | 16 |  | ASCII |  |
| 42210 | A4E2 | Key | 16 |  | ASCII |  |

# Table 1: Safety Standard

| Standard Number | Description in Protocol / Standard Name | City / Country | Current support (Three-Phase) | Current support (Single-Phase) |
| --- | --- | --- | --- | --- |
| 1 | AU AS/NZS 4777.2:2015 | Australia |  | Yes |
| 2 | NZ AS/NZS 4777.2:2015 | New Zealand |  | Yes |
| 3 | CN NB/T 32004:2018 | China |  | Yes |
| 4 | EN 50549-1:2019 | Europe / Global | Yes | Yes |
| 5 | NL EN 50549-1:2019 | Netherland | Yes | Yes |
| 6 | UK G98-1 | United Kingdom | Yes | Yes |
| 7 | UK G99-1 | United Kingdom | Yes | Yes |
| 8 | DE VDE-AR-N 4105:2018 | Germany | Yes | Yes |
| 9 | BR ABNT NBR 16149:2013 | Brazil |  | Yes |
| 10 | Mexico | Mexico |  | Yes |
| 11 | CN GB/T 37408:2019 | China |  |  |
| 12 | EN 50549-2:2019 | Global |  | Yes |
| 13 | IEC 61727 | Global | Yes | Yes |
| 14 | PL EN 50549-1:2019 | Poland | Yes | Yes |
| 15 | VN IEC 61727:2004 | Vietnam | Yes | Yes |
| 16 | LK IEC 61727:2004 | Sri Lanka |  | Yes |
| 17 | IT CEI 0-21:2019 | Italy | Yes | Yes |
| 18 | MA IEC 61727:2004 | Morocco |  | Yes |
| 19 | AR IEC 61727:2004 | Argentina |  | Yes |
| 20 | IT CEI 0-21:2019 ARetti | Italy | Yes |  |
| 21 | Italy 03 | Italy |  |  |
| 22 | ZA NRS 097-2-1:2017 | South Africa |  | Yes |
| 23 | BE C10/11:2019 | Belgium | Yes | Yes |
| 24 | DK1 EN 50549-1:2019 | Denmark (Western) | Yes |  |
| 25 | DK2 EN 50549-1:2019 | Denmark (Eastern) | Yes |  |
| 26 | IE EN 50549-1:2019 | Ireland |  |  |
| 27 | CL IEC 61727:2004 | Chile |  |  |
| 28 | RO EN 50549-1:2019 | Romania | Yes | Yes |
| 29 | HU EN 50549-1:2019 | Hungary | Yes | Yes |
| 30 | UL 1741:2010 | North America |  |  |
| 31 | AU A AS/NZS 4777.2:2020 | Australia |  | Yes |
| 32 | AU B AS/NZS 4777.2:2020 | Australia |  | Yes |
| 33 | AU C AS/NZS 4777.2:2020 | Australia |  | Yes |
| 34 | NZ 20 AS/NZS 4777.2:2020 | New Zealand |  | Yes |
| 35 | IT CEI 0-16:2019 | Italy | Yes |  |
| 36 | ES UNE 206007-1:2013 | Spain | Yes | Yes |
| 37 | BR LV ABNT 16149:2013 | Brazil |  |  |
| 38 | JO DC RFG:2015 | Jordan |  |  |
| 39 | FR VFR 2019 | France | Yes | Yes |
| 40 | FR Island 50Hz | France | Yes | Yes |
| 41 | FR Island 60Hz | France | Yes | Yes |
| 42 | LV EN 50549-1:2019 | Latvijas |  |  |
| 43 | SE EN 50549-1:2019 | Sweden | Yes |  |
| 44 | BR No.140:2022 | Brazil |  |  |
| 45 | CZ 01 EN 50549-1:2019 | Czech | Yes |  |
| 46 | CZ 02 EN 50549-1:2019 | Czech | Yes |  |
| 47 | NI G98/NI-1 | Nicaragua |  |  |
| 48 | NI G99/NI-1 | Nicaragua |  |  |
| 49 | PL B EN 50549-1:2019 | Poland |  |  |
| 50 | MEXICO_02 | Mexico 02 |  |  |
| 51 | TW_CNS_15382 | Taiwan |  |  |
| 52 | AT_TOR_Type_A | Austria 01 | Yes |  |
| 55 | CH A EN 50549-1 | Switzerland | YES |  |

# Table 2: Fault（Bit）

| Fault Code | Fault Description |
| --- | --- |
| Bit0 | MCU Fault |
| Bit1 | Current sensor fault |
| Bit2 | GFCI device fault |
| Bit3 | Relay fault |
| Bit4 | PV voltage high fault |
| Bit5 | ISO fault |
| Bit6 | GFCI fault |
| Bit7 | Temperature over fault |
| Bit8 | No utility fault |
| Bit9 | Grid voltage over fault |
| Bit10 | Grid frequency over fault |
| Bit11 | DCI over fault |
| Bit12 | Flash fault |
| Bit13 | Main and voice MCU communication fault |
| Bit14 | BUS voltage high fault |
| Bit15 | BUS voltage low fault |
| Bit16 | DRM S9 fault |
| Bit17 | DRM S0 fault |
| Bit18 | PE Connection missing |
| Bit19 | Bus voltage unbalance Bus |
| Bit20 | BMS communication fail |
| Bit21 | CT is not connected |
| Bit22 | CT reverse connection |
| Bit23 | Battery is not connected |
| Bit24 | Backup load over voltage |
| Bit25 | DC Art Fault |
| Bit26 | AFCI Self-Test Fault |
| Bit27 | Address assignment fault (Parallel system) |
| Bit28 | Battery precharge circuit fault |
| Bit29 | Battery protection GPIO fault |
| Bit30 | Shutdown circuit fault |
| Bit31 | Battery relay fault |
| Bit32 | Meter Communication Fault |
| Bit34 | CAN Communication Loss Fault at Parallel Mode for Slave |
| Bit35 | Get Master Fault Signal at Parallel Mode for Slave |
| Bit36 | Synchronization Signal Loss Fault at Parallel Mode for Slave |
| Bit39 | Slave Software Version Inconsistent with Master |
| Bit40 | Battery voltage exceeds the limit |
| Bit42 | Master and slave grid phase order is inconsistent in parallel mode |
| Bit43 | EPS Voltage exceeds the limit |
| Bit44 | Grid phase error |

# Table 3: Warning(Bit)

| Warning Code | Warning Description |
| --- | --- |
| Bit0 | PV1 over current |
| Bit1 | PV2 over current |
| Bit2 | PV3 over current |
| Bit3 | PV4 over current |
| Bit4 | PV1 under voltage |
| Bit5 | PV2 under voltage |
| Bit6 | PV3 under voltage |
| Bit7 | PV4 under voltage |
| Bit8 | BUS over voltage |
| Bit9 | BUS under voltage |
| Bit10 | INV over current |
| Bit11 | Anti-islanding protection |
| Bit12 | Grid peak over voltage |
| Bit13 | FW update |
| Bit14 | PE connection missing |
| Bit15 | Grid voltage consistency warning |
| Bit16 | Fan abnormal |
| Bit17 | Backup load overload warning |
| Bit18 | SPD failure warning |
| Bit28 | Battery over current |
| Bit35 | First connection grid parameters error |
| Bit37 | BUS voltage boost anomaly |
| Bit38 | Instantaneous overcurrent of EPS output current |

# Table 4: Exception(Three-phase)

| Exception Code | Exception Description |
| --- | --- |
| 1 | EXCEPTION_MCU |
| 2 | EXCEPTION_IPC |
| 3 | EXCEPTION_HW_SIGNAL_INV_CUR_ERROR |
| 5 | EXCEPTION_HW_SIGNAL_BUS_VOLT_ERROR |
| 6 | EXCEPTION_INV_CURR_HIGH |
| 8 | EXCEPTION_GRID_MISIING |
| 9 | EXCEPTION_GRID_VOLT_PEAK |
| 10 | EXCEPTION_GRID_VOLT |
| 11 | EXCEPTION_GRID_FREQ |
| 13 | EXCEPTION_GRID_10MIN_MEAN_ERROR |
| 15 | EXCEPTION_BUS_HIGH |
| 16 | EXCEPTION_BUS_LOW |
| 18 | EXCEPTION_ISLANDING |
| 20 | EXCEPTION_TEMP_HIGH |
| 21 | EXCEPTION_DCI |
| 22 | EXCEPTION_NVM_ERROR |
| 23 | EXCEPTION_HCT_DEVICE |
| 29 | EXCEPTION_RELAY |
| 34 | EXCEPTION_DRM_S9 |
| 35 | EXCEPTION_DRM_S0 |
| 37 | EXCEPTION_TEMP_LOW |
| 39 | EXCEPTION_LVRT |
| 40 | EXCEPTION_SHUT_DOWN |
| 42 | EXCEPTION_BUS_UNBALANCE |
| 45 | EXCEPTION_OFFGRID_CURR_INSTANT_HIGH |
| 46 | EXCEPTION_OFFGRID_CURR_RMS_HIGH |
| 47 | EXCEPTION_HW_MODE_SWITCH_ON2OFF_GRID |
| 48 | EXCEPTION_HW_MODE_SWITCH_OFF2ON_GRID |
| 49 | EXCEPTION_CT_NO_CONNECTION |
| 51 | EXCEPTION_BATT_SOC_LOW |
| 52 | EXCEPTION_EPS_OVER_POWER |
| 53 | EXCEPTION_REMOTE_SWITCH_SHUTDOWN |
| 55 | EXCEPTION_FIRST_GRID_PARA_ERROR |
| 101 | SLAVE_EXCEPTION_MCU |
| 102 | SLAVE_EXCEPTION_IPC |
| 103 | SLAVE_EXCEPTION_HW_SIGNAL_PV_CUR_ERROR |
| 104 | SLAVE_EXCEPTION_HW_SIGNAL_BUS_VOLT_ERROR |
| 106 | SLAVE_EXCEPTION_HW_SIGNAL_BATT_CUR_ERROR |
| 107 | SLAVE_EXCEPTION_PV_CURR_HIGH |
| 108 | SLAVE_EXCEPTION_PV_VOLT_HIGH |
| 109 | SLAVE_EXCEPTION_PV_VOLT_LOW |
| 110 | SLAVE_EXCEPTION_BATT_CURR_HIGH |
| 111 | SLAVE_EXCEPTION_BATT_VTG_HIGH |
| 112 | SLAVE_EXCEPTION_BATT_VTG_LOW |
| 113 | SLAVE_EXCEPTION_BUS_HIGH |
| 114 | SLAVE_EXCEPTION_BUS_LOW |
| 115 | SLAVE_EXCEPTION_GFCI |
| 116 | SLAVE_EXCEPTION_HCT_DEVICE |
| 118 | SLAVE_EXCEPTION_GFCI_DEVICE |
| 119 | SLAVE_EXCEPTION_BUS_RISE |
| 120 | SLAVE_EXCEPTION_ISO |
| 128 | SLAVE_EXCEPTION_FAN_ERROR |
| 130 | SLAVE_EXCEPTION_SHUT_DOWN |
| 133 | SLAVE_EXCEPTION_HW_SIGNAL_CAN_COMM_ERROR |
| 134 | SLAVE_EXCEPTION_CHIP1_ERROR |
| 135 | SLAVE_EXCEPTION_BATT_PRECHARGE_RELAY |
| 136 | SLAVE_EXCEPTION_BATT_RELAY |
| 137 | SLAVE_EXCEPTION_BATT_SHUT_DOWN |
| 139 | SLAVE_EXCEPTION_BATT_PROTECT_GPIO |
| 141 | SLAVE_EXCEPTION_BATT_PRECHARGE_CIRCUIT |
| 142 | SLAVE_EXCEPTION_PARALLEL_ADDR_ASSIGN |
| 143 | SLAVE_EXCEPTION_AFCI_DC_ARC |
| 144 | SLAVE_EXCEPTION_AFCI_SELFCHECK_ERROR |
| 145 | SLAVE_EXCEPTION_BMS_SOFT_RESET |

# Table 5: Exception(Single-phase)

| Exception Code | Exception Description |
| --- | --- |
| 1 | EXCEPTION_MCU |
| 2 | EXCEPTION_IPC |
| 3 | EXCEPTION_HW_SIGNAL_INV_CUR_ERROR |
| 4 | EXCEPTION_CODE_HW_SIGNAL_PV_CUR_ERROR |
| 5 | EXCEPTION_CODE_HW_SIGNAL_BUS_VOLT_ERROR |
| 6 | EXCEPTION_CODE_INV_CURR_HIGH |
| 7 | EXCEPTION_CODE_PV1_CURR_HIGH |
| 8 | EXCEPTION_CODE_GRID_MISIING |
| 9 | EXCEPTION_CODE_GRID_VOLT_PEAK |
| 10 | EXCEPTION_CODE_GRID_VOLT |
| 11 | EXCEPTION_CODE_GRID_FREQ |
| 12 | EXCEPTION_CODE_GRID_CONSISTENCY_ERROR |
| 13 | EXCEPTION_CODE_GRID_10_MIN_MEAN_ERROR |
| 14 | EXCEPTION_CODE_PV_VOLT_HIGH |
| 15 | EXCEPTION_CODE_BUS_HIGH |
| 16 | EXCEPTION_CODE_BUS_LOW |
| 17 | EXCEPTION_CODE_PV_VOLT_LOW |
| 18 | EXCEPTION_CODE_ISLANDING |
| 19 | EXCEPTION_CODE_GFCI |
| 20 | EXCEPTION_CODE_TEMP_HIGH |
| 21 | EXCEPTION_CODE_DCI |
| 22 | EXCEPTION_CODE_NVM_ERROR |
| 23 | EXCEPTION_CODE_HCT_DEVICE |
| 24 | EXCEPTION_CODE_NPE_LEVEL_1 |
| 25 | EXCEPTION_CODE_GFCI_DEVICE |
| 26 | EXCEPTION_CODE_BUS_RISE |
| 27 | EXCEPTION_CODE_ISO |
| 28 | EXCEPTION_CODE_EXTENAL_DOG_CHECK_ERROR |
| 29 | EXCEPTION_CODE_RELAY |
| 30 | EXCEPTION_CODE_HCT_DEVICE_FATAL |
| 31 | EXCEPTION_CODE_GFCI_DEVICE_FATAL |
| 32 | EXCEPTION_CODE_ISO_FATAL |
| 33 | EXCEPTION_CODE_RELAY_FATAL |
| 34 | EXCEPTION_CODE_DRM_S9 |
| 35 | EXCEPTION_CODE_DRM_S0 |
| 36 | EXCEPTION_CODE_FM_UPDATING |
| 37 | EXCEPTION_CODE_TEMP_LOW |
| 38 | EXCEPTION_CODE_FAN_ERROR |
| 39 | EXCEPTION_CODE_LVRT |
| 40 | EXCEPTION_CODE_SHUT_DOWN |
| 41 | EXCEPTION_CODE_NPE_LEVEL_2 |
| 42 | EXCEPTION_CODE_BUS_UNBALANCE |
| 43 | EXCEPTION_CODE_BAT_VOLT_HIGH |
| 44 | EXCEPTION_CODE_BAT_VOLT_LOW |
| 45 | EXCEPTION_CODE_BAT_CURR_HIGH |
| 46 | EXCEPTION_CODE_HW_SIGNAL_BAT_CUR_ERROR |
| 47 | EXCEPTION_CODE_CAN_ERROR |
| 48 | EXCEPTION_CODE_CT_NULL |
| 49 | EXCEPTION_CODE_CT_REVERSE |
| 50 | EXCEPTION_CODE_BAT_NULL |
| 51 | EXCEPTION_CODE_EPS_OVER_LOAD |
| 52 | EXCEPTION_CODE_RESTART |
| 53 | EXCEPTION_CODE_BREAK_BAT_RELAY |
| 54 | EXCEPTION_CODE_PV2_CURR_HIGH |
| 55 | EXCEPTION_CODE_PV3_CURR_HIGH |
| 56 | EXCEPTION_CODE_DC_ARC |
| 57 | EXCEPTION_CODE_AFCI_SELFTEST |
| 58 | EXCEPTION_CODE_ADDR_ASSIGNMENT |
| 59 | EXCEPTION_CODE_PRECHRG_CIRCUIT |
| 60 | EXCEPTION_CODE_PROTECT_GPIO |
| 61 | EXCEPTION_CODE_SHUTDOWN_CIRCUIT |
| 62 | EXCEPTION_CODE_BATT_RELAY |
| 63 | EXCEPTION_CODE_GRID_CHECK_ERROR |
| 67 | EXCEPTION_CODE_METER_COMM_ERROR |
| 68 | EXCEPTION_CODE_BMS_SOFT_RESET |
| 69 | EXCEPTION_CODE_PARALLEL_VERSION_ERR |
| 101 | EXCEPTION_CODE_OFF-GRID__MISSING_PROTECTION_1 |
| 102 | EXCEPTION_CODE_OFF-GRID__MISSING_PROTECTION_2 |
| 103 | EXCEPTION_CODE_OFF-GRID__RESTORE_PROTECTION |
| 104 | EXCEPTION_CODE_STANDBY |
| 105 | EXCEPTION_CODE_OFF-GRID__MISSING_PROTECTION_3 |
| 106 | EXCEPTION_CODE_OFF-GRID__MISSING_PROTECTION_4 |
| 107 | EXCEPTION_CODE_BATMODESWITCH_PROTECTION |
| 108 | EXCEPTION_CODE_SHUT_DOWN |
| 109 | EXCEPTION_CODE_EPO |
| 110 | EXCEPTION_CODE_BMSABLE |
| 111 | EXCEPTION_CODE_BMSDISABLE |
| 112 | EXCEPTION_CODE_RESTART |
| 113 | EXCEPTION_CODE_SAFETYSWITCH |

APPING EXAMPLE

| Example | Bytes | Corresponding Value |
| --- | --- | --- |
| Device Address | 1 | 0x01 |
| Function Code | 2 | 0x03 |
| Register Address | 2 | 0x75 0x3A |
| Read Length | 2 | 0x00 0x10 |
| CRC Value | 2 | 0x7E 0x07 |